## 棒形支柱复合主要尺寸与特性绝缘子
12kV-252kV棒形支柱复合绝缘子主要尺寸与特性
Main dimension and characteristic of 12kV-252kV solid-core post composite insulator
NO. | type | fig | Ur 额定 电压 Rated voltage kV | 额定 弯曲负荷 Rated bending load kN | 额定 扭转负荷Rated torsion load kN.m | H 高度 height mm | 公称 爬电距离 Normal creepage distance mm | 伞径 Dia. Of shed mm | 上附件安装 尺寸（孔数n1-孔径 d1-孔中心圆 直径a1)Assembly dimension of upper fitting | 下附件安装尺寸 (孔数n2-孔径d2- 孔中心圆 直径a2) Assembly dimension of lower fitting | 工频 湿耐受kV(有效值）power frequency wet withstand voltage(effective value) | 雷电全 波冲击电压（峰值）kV Lightning full wave impulse voltage (effective value)
序号 | 产品型号 | 图号
1 | FZSW1-12/4 |  | 12 | 4 | 0.6 | 215 | 250 | ￠90 | 4-M12-￠76 | 4-￠13-￠76 | 30 | 75
2 | FZSW1-24/8 |  | 24 | 8 | 1.2 | 350 | 450 | ￠131 | 4-M12-￠140 | 4-M12-￠210 | 50 | 125
3 | FZSW2-40.5/6L |  | 40.5 | 6 | 1.5 | 445 | 1020 | ￠131/￠135 | 4-M12-￠76 | 4-M12-￠76 | 90 | 200
4 | FZSDW6-126/10 |  | 126 | 10 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠127 | 4-￠18-￠178 | 230 | 500
6 | FZSW6-126/10 |  | 126 | 10 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠127 | 4-￠18-￠178 | 230 | 500
7 | [5 empty] | 1150 | 2600
8 | [5 empty] | 1100 | 2460
9 | [5 empty] | 1060 | 2420
10 | FZSW6-126/10K |  | 126 | 10 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠127 | 4-￠18-￠178 | 230 | 500
11 | [5 empty] | 1220 | 2730
12 | [5 empty] | 1150 | 2600
13 | [5 empty] | 1100 | 2460
14 | [5 empty] | 1060 | 2420
15 | FZSW6-126/10 |  | 126 | 10 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠140 | 4-￠18-￠178 | 230 | 500
16 | [5 empty] | 1200 | 2730
17 | [5 empty] | 1150 | 2600
18 | [5 empty] | 1100 | 2460
19 | [5 empty] | 1060 | 2420
20 | FZSW6-126/10K |  | 126 | 10 | 6 | 1220 | 2750 |  | 4-￠13-￠40 | 4-￠18-￠178 | 230 | 500
21 | [5 empty] | 1200 | 2730
22 | [5 empty] | 1150 | 2600
23 | [5 empty] | 1100 | 2460
24 | [5 empty] | 1060 | 2420

## 3
12kV-252kV棒形支柱复合绝缘子主要尺寸与特性
Main dimension and characteristic of 12kV-252kV solid-core post composite insulator
NO. | type | fig | 额定 电压 Rated voltage kV | 额定 弯曲负荷 Rated bending load kN | 额定 扭转负荷 Rated torsion load kN.m | H 高度 Height mm | 公称 爬电距离 Normal creepage distance mm | 伞径 Dia.of shed mm | 上附件安装 尺寸（孔数n1-孔径 d1-孔中心圆直径a1) Assembly dimension of upper fitting | 下附件安装尺寸 (孔数n2-孔径d2- 孔中心圆直径a2) Assembly dimension of lower fitting | 工频 湿耐受kV(有效值）power frequency wet withstand voltage (effective value) | 雷电全 波冲击电压（峰值） Lightning full wave impulse voltage (effective value)kV
序号 | 产品型号 | 图号
25 | FZSW6-126/12.5 |  | 126 | 12.5 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠127 | 4-￠18-￠225 | 230 | 500
26 | [5 empty] | 1200 | 2730
27 | [5 empty] | 1150 | 2600
28 | [5 empty] | 1060 | 2420
29 | FZSW6-126/12.5K |  | 126 | 12.5 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠127 | 4-￠18-￠225 | 230 | 500
30 | [5 empty] | 1200 | 2730
31 | [5 empty] | 1150 | 2600
32 | [5 empty] | 1100 | 2460
33 | [5 empty] | 1060 | 2420
34 | FZSW6-126/12.5 |  | 126 | 12.5 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠127 | 4-￠18-￠225 | 230 | 500
35 | [5 empty] | 1200 | 2730
36 | [5 empty] | 1150 | 2600
37 | [5 empty] | 1100 | 2460
38 | [5 empty] | 1060 | 2420
39 | FZSW6-126/12.5K |  | 126 | 12.5 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠127 | 4-￠18-￠270 | 230 | 500
40 | [5 empty] | 1200 | 2730
41 | [5 empty] | 1150 | 2600
42 | [5 empty] | 1100 | 2460
43 | [5 empty] | 1060 | 2420
44 | FZSW6-126/12.5 |  | 126 | 12.5 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠127 | 4-￠18-￠270 | 230 | 500
45 | [5 empty] | 1200 | 2730
46 | [5 empty] | 1150 | 2600
47 | [5 empty] | 1100 | 2460
48 | [5 empty] | 1060 | 2420
49 | FZSW6-126/12.5K |  | 126 | 12.5 | 6 | 1220 | 2750 | ￠190 | 4-￠13-￠127 | 4-￠18-￠270 | 230 | 500
50 | [5 empty] | 1200 | 2730
51 | [5 empty] | 1150 | 2600
52 | [5 empty] | 1100 | 2460
53 | [5 empty] | 1060 | 2420
54 | FZSW6-126/12.5 |  | 126 | 12.5 | 6 | 1220 | 2750 | ￠190 | 4-M12-￠140 | 4-￠18-￠270 | 230 | 500
55 | [5 empty] | 1200 | 2730
56 | [5 empty] | 1150 | 2600
57 | [5 empty] | 1100 | 2460
58 | [5 empty] | 1060 | 2420

## S
12kV～252kV棒形支柱复合绝缘子
12KV -252kV solid-core post composite insulator
电站用12 | kV～252kV棒形支柱 |  | 交流系统中运行的电力
设备和装置，尤其适用于污秽地区，能有效地防止污闪事故，减少运行中维护工作量，是一种
性能优良的新一代绝缘子产品 |  |  | 。
棒形支柱 | 复合绝缘子 | 伞群具有良好憎水性，此外，伞群还具有良好的抗老化性能，经1000h人工加速老化试验和数年自然老
化试验和10年的远行经验表明：其性能无明显下降。棒形支柱复合绝缘子机 性能主要由芯棒（材料为环氧玻纤 |  |  |  |  | 引拨棒）承担
。其抗张和抗弯＞500Mp,是高强度瓷材料的5～10倍，且分散性及小，变异系数在3％以内 ，可靠性高。
棒形支柱复合绝缘子 |  | 具有体积小，重量轻（仅为瓷绝缘子的/3—1/5），不易破碎等特点，给运输、安装、维护带来极大方便，并具有良好的抗震性。其主要尺寸
与特性见表
ALL rod post composite insulator with voltage of 12kV～252kV used in power equipment and |  |  |  | 252kV,used at,a.c systems of 10kV | ～220kV,are of
generation insulator ,suitable for service at polluted regions for successive preventing from | [5 empty] | pollusion
flashover and reducing maintanence work.
The post composite insulation shed has well htdropphobicity and degradtion resistance and well anti-ageing,
articial ageing for 1000h test and natural ageing test for years and ten years experiences show: no obvious reduction in performance.
its tensile and bending strength is higher than 500Mp,and is 5-10 times of that of high-strength porcelain material, and with small dispersion, and the variation factor is within 3%, and with high reliability.
Composite post insulator is characteristic of small size ,light (1/3-1/5 of weight of porecelain)
which is convenient to handle ,mount and transport, and with excellent anti-explosive. The demension and characteristic are given in Tab 8

## 4
COMPOSITE INSULATOR 复合绝缘子
12kV-252kV耐污型棒形支柱复合绝缘子主要尺寸与特性
Main dimension and characteristic of 12kV-252kV and pollution-type solid-core post composite insulator
NO. | type | fig | 额定 电压 Rated voltage kV | 额定 弯曲负荷 Rated bending load kN | 额定 扭转负荷 Rated torsion load kN.m | H 高度 Height mm | 公称 爬电距离 Normal creepage distance mm | 伞径 Dia. Of shed mm | 上附件安装 尺寸（孔数n1-孔径 d1-孔中心圆直径a1) Assembly dimension of upper fitting | 下附件安装尺寸 (孔数n2-孔径d2- 孔中心圆直径a2)Assembly dimension of lower fitting | 工频 湿耐受kV(有效值）Power frequency wet withstand voltage (effective value) | 雷电全 波冲击电压（峰值）Lightning full wave impulse voltage(effective value)kV
序号 | 产品型号 | 图号
59 | FZSW6-126/12.5K |  | 126 | 12.5 | 6 | 1220 | 2750 | ￠190 | 4-￠13-￠140 | 4-￠18-￠270 | 230 | 500
60 | [5 empty] | 1200 | 2730
61 | [5 empty] | 1150 | 2600
62 | [5 empty] | 1100 | 2460
63 | [5 empty] | 1060 | 1060
64 | FZSW8-126/10 |  | 126 | 10 | 6 | 1220 | 3650 | ￠215 | 4-M12-￠140 | 4-￠18-￠178 | 250 | 500
65 | FZSW8-126/10K |  | 126 | 10 | 6 | 1200 | 3630 | ￠215 | 4-M12-￠140 | 4-￠18-￠178 | 250 | 500
66 | [5 empty] | 1150 | 3550 | ￠215 | 4-M12- ￠140 | 4-￠18- ￠178 | 250 | 500
67 | FZSW8-126/10K |  | 126 | 12.5 | 6 | 1220 | 3650 | ￠215 | 4-￠13-￠140 | 4-￠18-￠178 | 230 | 500
68 | [5 empty] | 1200 | 3630
69 | [5 empty] | 1150 | 3550
70 | FZSW8-126/12.5 |  | 126 | 12.5 | 6 | 1220 | 3650 | ￠215 | 4-M12-￠140 | 4-￠18-￠225 | 230 | 500
71 | [5 empty] | 1200 | 3630
72 | [5 empty] | 1150 | 3550
73 | FZSW8-126/12.5K |  | 126 | 12.5 | 6 | 1220 | 3650 | ￠215 | 4-￠13-￠140 | 4-￠18-￠225 | 230 | 500
74 | [5 empty] | 1200 | 3630
75 | [5 empty] | 1150 | 3550
76 | FZSW8-126/12.5 |  | 126 | 12.5 | 6 | 1220 | 3650 | ￠215 | 4-M12-￠140 | 4-￠18-￠270 | 230 | 500
77 | [5 empty] | 1200 | 3630
78 | [5 empty] | 1150 | 3550
79 | FZSW8-126/12.5K |  | 126 | 12.5 |  | 1220 | 3650 | ￠215 | 4-￠13-￠140 | 4-￠18-￠270 | 250 | 500
80 | [5 empty] | 1200 | 3630
81 | [5 empty] | 1150 | 3550
82 | FZSW1-252/8 |  | 252 | 8 | 6 | 2370 | 7060 | ￠210 | 4-M12-￠140 | 4-￠18-￠225 | 500 | 1000
83 | FZSW1-252/8 |  | 252 | 8 | 6 | 2300 | 6950 | ￠215 | 4-M12-￠140 | 4-￠18-￠225 | 500 | 1000
84 | FZSW1-252/8K |  | 252 | 8 | 6 | 2370 | 7060 | ￠215 | 4-￠13- ￠140 | 4-￠18- ￠225 | 500 | 1000
85 | [5 empty] | 2300 | 6950
86 | FZSW1-252/8 |  | 252 | 8 | 6 | 2370 | 7060 | ￠215 | 4-M12-￠140 | 4-￠18-￠270 | 500 | 1000
87 | [5 empty] | 2300 | 6950 | ￠215 | 4-M12-￠140 | 4-￠18-￠270
88 | FZSW1-252/8K |  | 252 | 8 | 6 | 2370 | 7060 | ￠215 | 4-M12-￠140 | 4-￠18-￠270 | 500 | 1000
89 | [5 empty] | 2300 | 6950 | ￠215 | 4-￠13-￠140 | 4-￠18-￠270 | 500 | 1000

## 复合绝缘子5
耐污型复合绝缘子图样和型号说明 drawing and instruction of type of anti-pollution composite insulator
型号说明:FZSCW1-126/12.5K-Z
FZS—棒形支柱复合绝缘子； |  | Note:
C—瓷质芯棒（可缺省） |  | Example :FZSCW1-1269/12.5K-Z
| w—防污型 | FZS-solid-core post composite insulator
| 1—设计序号 | C-porcelain core(may be omitted)
| 126—额定电压 | W-anti-pollution type
| 12.5—额定机械破坏负荷 | 1-design number
| K—两端连接方式 | 126-rated voltage
| 12.5-额定机 弯曲负荷 | 12.5-rated mechanical failing load
| Z-直流系统用（交流系统缺省 | K-Two tops-connecting method
Z0-DC(omit if AC)